## SphereGap
Sphere Gap Breakdown Voltage Tables
The following two tables give the breakdown voltages for a standard sphere gap of the specified sphere size and spacing.
The standard accuracy is down voltages for a standard sphere gap of the specified sphere size and spacing. The standard accuracy is ±4%
sphere gap construction and procedures is available.
Sphere gap with one terminal grounded
A -> AC, DC, either polarity and full negative standard impulse voltages (one sphere grounded)
B -> positive polarity standard impulse voltages and impulse voltages with long tails (either polarity)
Sphere Diameter (cm)
Gap Spacing | 5 |  | 10 |  | 15 |  | 25 |  | 50 |  | 100 |  | 150 |  | 200
cm | A | B | A | B | A | B | A | B | A | B | A | B | A | B | A | B
0.5 | 17.4 | 17.4 | 16.9 | 16.8 | 16.9 | 16.9
1 | 32 | 32 | 31.7 | 31.7 | 31.4 | 31.4 | 31.2 | 31.4
1.5 | 44.7 | 45.5 | 44.7 | 45.1 | 44.7 | 45.1 | 44.7 | 44.7
2 | 57.5 | 58 | 58 | 58 | 58 | 58 | 58 | 58
2.5 |  |  | 71.5 | 71.5 | 71.5 | 71.5 | 71.5 | 71.5 | 71.5 | 71.5
3 |  |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
3.5 |  |  | 95.5 | 96 | 97 | 97 | 97 | 97 | 97 | 97
4 |  |  | 106 | 108 | 108 | 110 | 110 | 110 | 110 | 110
5 |  |  | 123 | 127 | 127 | 132 | 135 | 136 | 136 | 136
7.5 |  |  |  |  | 181 | 187 | 195 | 196 | 199 | 199
10 | [6 empty] | 257 | 268 | 259 | 259 | 262 | 262 | 262 | 262 | 262 | 262
12.5 | [6 empty] | 277 | 294 | 315 | 317
15 | [6 empty] | 309 | 331 | 367 | 974 | 383 | 384 | 384 | 384 | 384 | 384
17.5 | [6 empty] | 336 | 362 | 413 | 425
20 | [8 empty] | 452 | 472 | 500 | 500 | 500 | 500 | 500 | 500
25 | [8 empty] | 520 | 545 | 605 | 610
30 | [8 empty] | 575 | 610 | 700 | 715 | 730 | 735 | 735 | 740
35 | [8 empty] | 725 | 755 | 785 | 800
40 | [10 empty] | 862 | 885 | 940 | 950 | 960 | 965
45 | [10 empty] | 925 | 965
50 | [10 empty] | 1000 | 1020 | 1110 | 1130 | 1160 | 1170
75 | [10 empty] | 1210 | 1260 | 1420 | 1460 | 1510 | 1590
100 | [14 empty] | 1870 | 1900
symmetrical sphere gaps
20deg C, 760 torr, either polarity impulse, AC, DC
spacings <0.5D Accuracy +/- 3% ; spacings >=0.5D accuracy +/- 5%
Sphere Diameter (cm)
gap (cm) | 5 | 10 |  | 15 | 25 | 50 | 100 | 150 | 200
0.5 | 17.5 | 16.9 |  | 16.5
1 | 32.2 | 31.6 |  | 31.3 | 31
1.5 | 46.1 | 45.8 |  | 45.5 | 45
2 | 58.3 | 59.3 |  | 59.2 | 59
2.5 | 69.4 | 72.4 |  | 72.9 | 73
3 | 79.3 | 84.9 |  | 85.8 | 86
4 |  | 107 |  | 111 | 113 | 112
5 |  | 128 |  | 134 | 138 | 138 | 137 | 137 | 137
8 |  | 177 |  | 194 | 207 | 214
10 |  |  |  |  | 248 | 263 | 266 | 267 | 267
12 |  |  |  |  | 286 | 309
14 |  |  |  |  | 320 | 353
16 |  |  |  |  | 352 | 394
18 | [5 empty] | 452
20 | [5 empty] | 495 | 504 | 511 | 511
25 | [5 empty] | 558 | 613 | 628 | 632
30 | [6 empty] | 744 | 741 | 746
35 | [6 empty] | 812 | 848 | 860
40 | [6 empty] | 902 | 950 | 972
50 | [6 empty] | 1070 | 1140 | 1180
60 | [6 empty] | 1210 | 1320 | 1380
70 | [7 empty] | 1490 | 1560
80 | [7 empty] | 1640 | 1730
90 | [8 empty] | 1900
100 | [8 empty] | 2050
Copyright 1998, Jim Lux / spherev.htm / 5 May 1998 /
Spark Gap Correction Factors
Effects of atmospheric conditions
V = k* V0
where k is a function of the air density d
d = p/760 * (293 / (273+T)) where p in Torr and T in degrees C
d | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1 | 1.05 | 1.1 | 1.15
k | 0.72 | 0.77 | 0.82 | 0.86 | 0.91 | 0.95 | 1 | 1.05 | 1.09 | 1.12
The voltage increases with humidity varying some 2-3% over a normal atmospheric range of 8-15 g/m3.
Irradiation
If the gap is illuminated with UV or X-rays, it is more easily ionized. The effect is more pronounced with smaller gaps, a 20% reduction
for short gaps of a few cm when irradiated. For this reason, UV irradiation is specified for accurate breakdown voltage

## RodGap
Rod Gap Breakdown Voltage Tables
More details on Rod Gap procedures and construction
The following table values valid for:
1.27 cm square rods
27 deg C
760 torr (1013 mBar)
15.5 torr water vapor pressure
(11 g/cc water content for impulses).
The voltages in the table reflect the breakdown of the rod gap +/- 8%
Rod Gap | Voltage | 1/5 uSec | 1/5 uSec | 1/50 uSec | 1/50 uSec
Spacing |  | Pos impulse | Neg impulse | Pos impulse | Neg impulse
cm | kV | kV | kV | kV | kV
2 | 26
4 | 47
6 | 62
8 | 72
10 | 81 | 101 | 111 | 90 | 97
15 | 102
20 | 124 | 179 | 208 | 160 | 178
25 | 147
30 | 172 | 256 | 301 | 226 | 262
40 | 225 | 348 | 392 | 279 | 339
50 | 278 | 431 | 475 | 334 | 407
60 | 332 | 513 | 557 | 397 | 470
70 | 382
80 | 435 | 657 | 701 | 511 | 585
90 | 488
100 | 537 | 820 | 855 | 629 | 703
Humidity Correction
H20 Vapor Press. (torr) | 2.5 | 5 | 10 | 15 | 20 | 25 | 30
Correction Factor % | -16.5 | -13.1 | -6.5 | -0.5 | 4.4 | 7.9 | 10.1
Data taken from tables and graphs in Naidu & Kamaraju, High Voltage Engineering.
Copyright 1998, Jim Lux / rodv.htm / 5 May 1998 / Back to HV Home / Back to home page / Mail to Jim

## SparkGap
SPARK-GAP VOLTAGES
Based on results of the American Institute of Electric Engineers
Air at 760 mmHg, 25 C
Diameter of spherical electrodes, [cm]
Peak Volt | Needle | 2.5 | 5 | 10 | 25
Length of spark gap
[kV] | [cm] | [cm] | [cm] | [cm] | [cm]
5 | 0.42 | 0.13 | 0.15 | 0.15 | 0.16
5.9302 | 0.5
10 | 0.85 | 0.27 | 0.29 | 0.3 | 0.32
11.6667 | 1
15 | 1.3 | 0.42 | 0.44 | 0.46 | 0.48
20 | 1.75 | 0.58 | 0.6 | 0.62 | 0.64
22.7778 | 2
25 | 2.2 | 0.76 | 0.77 | 0.78 | 0.81
30 | 2.69 | 0.95 | 0.94 | 0.95 | 0.98
33.0392 | 3
35 | 3.2 | 1.17 | 1.12 | 1.12 | 1.15
40 | 3.81 | 1.41 | 1.3 | 1.29 | 1.32
41.3971 | 4
45 | 4.49 | 1.68 | 1.5 | 1.47 | 1.49
48.5915 | 5
50 | 5.2 | 2 | 1.71 | 1.65 | 1.66
54.9689 | 6
60 | 6.81 | 2.82 | 2.17 | 2.02 | 2.01
60.95 | 7
65.95 | 8
70 | 8.81 | 4.05 | 2.68 | 2.42 | 2.37
70.8297 | 9
75.1965 | 10
79.5633 | 11
80 | 11.1 |  | 3.26 | 2.84 | 2.74
84.0909 | 12
88.6364 | 13
90 | 13.3 |  | 3.94 | 3.28 | 3.11
93.1818 | 14
97.7273 | 15
100 | 15.5 |  | 4.77 | 3.75 | 3.49
102.2727 | 16
106.8182 | 17
110 | 17.7 |  | 5.79 | 4.25 | 3.88
111.4286 | 18
116.1905 | 19
120 | 19.8 |  | 7.07 | 4.78 | 4.28
120.9091 | 20
125.4545 | 21
130 | 22 |  |  | 5.35 | 4.69
134.7619 | 23
139.5238 | 24
140 | 24.1 |  |  | 5.97 | 5.1
144.5 | 25
149.5 | 26
150 | 26.1 |  |  | 6.64 | 5.52
154.5 | 27
159.5 | 28
160 | 28.1 |  |  | 7.37 | 5.95
164.5 | 29
169.5 | 30
170 | 30.1 |  |  | 8.16 | 6.39
174.7368 | 31
180 | 32 |  |  | 9.03 | 6.84
185.2632 | 33
190 | 33.9 |  |  | 10 | 7.3
190.5556 | 34
196.1111 | 35
200 | 35.7 |  |  | 11.1 | 7.76
201.5789 | 36
206.8421 | 37
210 | 37.6 |  |  | 12.3 | 8.24
212.1053 | 38
217.3684 | 39
220 | 39.5 |  |  | 13.7 | 8.73
222.6316 | 40
227.8947 | 41
230 | 41.4 |  |  | 15.3 | 9.24
233.1579 | 42
238.4211 | 43
240 | 43.3 |  |  |  | 9.76
243.6842 | 44
248.9474 | 45
250 | 45.2 |  |  |  | 10.3
259.4737 | 47
270 | 49
275.2632 | 50
300 | 54.7 |  |  |  | 13.3
CORRECTIONS FOR TEMPERATURE AND PRESSURE
Values found in the above table may be corrected for temperature and pressure
by multiplying the values given by the appropriate correction factor found below:
Pressure [mmHg]
Temp. [C] | 720 | 740 | 760 | 780
0 | 1.04 | 1.06 | 1.09 | 1.12 |  | kV | cm
10 | 1 | 1.02 | 1.05 | 1.08 |  | 20 | 1.75
20 | 0.96 | 0.99 | 1.015 | 1.04 |  | 22.7778 | 2 | Interpolation
30 | 0.93 | 0.96 | 0.98 | 1.01 |  | 25 | 2.2
Interpolation for needle-points |  |  |  | Interpolation for 5cm balls
kV | cm |  |  | kV | cm
20 | 1.75 | Fixpoint 1 |  | 30 | 0.94 | Fixpoint 1
22.6596 | 2 | Interpolation |  | 31.6667 | 1 | Interpolation
30 | 2.69 | Fixpoint 2 |  | 40 | 1.3 | Fixpoint 2

## SparkGap (2)
SPARK-GAP VOLTAGES | [5 empty] | Based on results of the American Institute of Electric Engineers
interpolated values:
Air at 760 mmHg, 25 C | [6 empty] | Air at 760 mmHg, 25 C
|  | Diameter of spherical electrodes, [cm] | [6 empty] | Diameter of spherical electrodes, [cm]
Peak Volt | Needle | 2.5 | 5 | 10 | 25 |  | Peak Volt | Needle | 2.5 | 5 | 10 | 25
|  |  | Length of spark gap | [6 empty] | Length of spark gap
[kV] | [cm] | [cm] | [cm] | [cm] | [cm] |  | [kV] | [cm] | [cm] | [cm] | [cm] | [cm]
5 | 0.42 | 0.13 | 0.15 | 0.15 | 0.16 |  | 130 | 22 |  |  | 5.35 | 4.69
5.9302 | 0.5 | [5 empty] | 134.7619 | 23
10 | 0.85 | 0.27 | 0.29 | 0.3 | 0.32 |  | 139.5238 | 24
11.6667 | 1 | [5 empty] | 140 | 24.1 |  |  | 5.97 | 5.1
15 | 1.3 | 0.42 | 0.44 | 0.46 | 0.48 |  | 144.5 | 25
20 | 1.75 | 0.58 | 0.6 | 0.62 | 0.64 |  | 149.5 | 26
22.7778 | 2 | [5 empty] | 150 | 26.1 |  |  | 6.64 | 5.52
25 | 2.2 | 0.76 | 0.77 | 0.78 | 0.81 |  | 154.5 | 27
30 | 2.69 | 0.95 | 0.94 | 0.95 | 0.98 |  | 159.5 | 28
33.0392 | 3 | [5 empty] | 160 | 28.1 |  |  | 7.37 | 5.95
35 | 3.2 | 1.17 | 1.12 | 1.12 | 1.15 |  | 164.5 | 29
40 | 3.81 | 1.41 | 1.3 | 1.29 | 1.32 |  | 169.5 | 30
41.3971 | 4 | [5 empty] | 170 | 30.1 |  |  | 8.16 | 6.39
45 | 4.49 | 1.68 | 1.5 | 1.47 | 1.49 |  | 174.7368 | 31
48.5915 | 5 | [5 empty] | 180 | 32 |  |  | 9.03 | 6.84
50 | 5.2 | 2 | 1.71 | 1.65 | 1.66 |  | 185.2632 | 33
54.9689 | 6 | [5 empty] | 190 | 33.9 |  |  | 10 | 7.3
60 | 6.81 | 2.82 | 2.17 | 2.02 | 2.01 |  | 190.5556 | 34
60.95 | 7 | [5 empty] | 196.1111 | 35
65.95 | 8 | [5 empty] | 200 | 35.7 |  |  | 11.1 | 7.76
70 | 8.81 | 4.05 | 2.68 | 2.42 | 2.37 |  | 201.5789 | 36
70.8297 | 9 | [5 empty] | 206.8421 | 37
75.1965 | 10 | [5 empty] | 210 | 37.6 |  |  | 12.3 | 8.24
79.5633 | 11 | [5 empty] | 212.1053 | 38
80 | 11.1 |  | 3.26 | 2.84 | 2.74 |  | 217.3684 | 39
84.0909 | 12 | [5 empty] | 220 | 39.5 |  |  | 13.7 | 8.73
88.6364 | 13 | [5 empty] | 222.6316 | 40
90 | 13.3 |  | 3.94 | 3.28 | 3.11 |  | 227.8947 | 41
93.1818 | 14 | [5 empty] | 230 | 41.4 |  |  | 15.3 | 9.24
97.7273 | 15 | [5 empty] | 233.1579 | 42
100 | 15.5 |  | 4.77 | 3.75 | 3.49 |  | 238.4211 | 43
102.2727 | 16 | [5 empty] | 240 | 43.3 |  |  |  | 9.76
106.8182 | 17 | [5 empty] | 243.6842 | 44
110 | 17.7 |  | 5.79 | 4.25 | 3.88 |  | 248.9474 | 45
111.4286 | 18 | [5 empty] | 250 | 45.2 |  |  |  | 10.3
116.1905 | 19 | [5 empty] | 259.4737 | 47
120 | 19.8 |  | 7.07 | 4.78 | 4.28 |  | 270 | 49
120.9091 | 20 | [5 empty] | 275.2632 | 50
125.4545 | 21 | [5 empty] | 300 | 54.7 |  |  |  | 13.3
CORRECTIONS FOR TEMPERATURE AND PRESSURE (k_needle)
Values found in the above table may be corrected for temperature and pressure
by multiplying the values given by the appropriate correction factor found below:
| Pressure [mmHg] | [5 empty] | actual P
| Temp.[C] | 720 | 740 | 760 | 780 |  | 750
| 0 | 1.0321 | 1.0581 | 1.0841 | 1.1102 |  | 1.0711 |  | Interpolation for 5cm balls
| 10 | 0.99902 | 1.0241 | 1.0492 | 1.0743 |  | 1.0367 |  | kV | cm
| 20 | 0.96819 | 0.99243 | 1.0167 | 1.0409 |  | 1.0045 |  | 30 | 0.94 | Fixpoint 1
| 30 | 0.93939 | 0.96283 | 0.98627 | 1.0097 |  | 0.97455 |  | 31.6667 | 1 | Interpolation
actual T: | 25 | 0.95355 | 0.97738 | 1.0012 | 1.025 |  | 0.98929 |  | 40 | 1.3 | Fixpoint 2
table above:
Jim Lux's original tried to fit in formulas,
as follows (see SphereGap sheet!):
Effects of atmospheric conditions
V = k* V0 <--- voltage correction
where k is a function of the air density d
d = p/760 * (293 / (273+T))
where p in Torr and T in degrees C
The little k vs. d table below was fitted to:
k = 0.0937 + 0.90303 * d
This value of k had to be corrected by
k_needle = k * 1.02 ,in order to
approximate the original needle point table
The formulas can be compressed in one, which was used in my new needle-point table above,
which, however minor, I feel, might give smoother and more logical values, than the original table.
k_needle = 1.02*(0.0937+((Ptorr/760)*(293/(273+TempC)))*0.90303)
| d | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1 | 1.05 | 1.1 | 1.15
| k | 0.72 | 0.77 | 0.82 | 0.86 | 0.91 | 0.95 | 1 | 1.05 | 1.09 | 1.12
The voltage increases with humidity varying some 2-3% over a normal atmospheric range of 8-15 g/m3.
Irradiation
If the gap is illuminated with UV or X-rays, it is more easily ionized. The effect is more pronounced with smaller gaps, a 20% reduction
for short gaps of a few cm when irradiated. For this reason, UV irradiation is specified for accurate breakdown voltage
| Original poster: "Jim Lux by way of Terry Fritz <twftesla@qwest.net>" | [7 empty] | 2001-11-18
<jimlux@earthlink.net>
The Handbook of Chemistry and Physics (some editions, anyway) has a needle
gap table*. The needles are #00 sewing needles, by the way. The needles need
to be sharp, and a fair ways (say 10 times the spacing) from any metal
object.
5kV 0.42 cm
10kV 0.85 cm
15kV 1.30 cm
20kV 1.75 cm
25 kV 2.20 cm
You'll note it's not linear, and giving the distances to two places is
somewhat spurious, because I'd be surprised if the accuracy of this is 10%.
Note, use the peak of the AC voltage! i.e. 11kV RMS = 1.414*11 or 15 kV
peak.
Small sphere are easy to come by... look for solid brass drawer pulls.
Perfect spheres aren't necessary, just get close.
*This table is at:
http://hot-streamer.com/TeslaCoils/Misc/SGapVolt.jpg

## Fit1
SPARK-GAP VOLTAGES
C:\TCWIN4\CLIPBRD.WK1 |  |  | y=a+bx^(0.5)+cx+dx^(1.5)+ex^2+fx^(2.5)+gx^3
|  | Parameters | Values | Std Error | T Value | 95% Conf Lim | 95% Conf Lim
Eqn | y=a+bx^(0.5)+cx+dx^(1.5)+ex^2+fx^(2.5)+gx^3 | a | 11.0269 | 1.1955 | 9.224 | 8.6432 | 13.4105
Eqn # | 6702 | b | -38.1022 | 2.8801 | -13.2296 | -43.8448 | -32.3595
r2 | 0.99999 | c | 57.6261 | 2.5033 | 23.0197 | 52.6346 | 62.6177
DF Adj r2 | 0.99999 | d | -23.1366 | 1.0334 | -22.3895 | -25.1971 | -21.0762
Fit Std Err | 0.2475 | e | 4.6224 | 0.21888 | 21.1188 | 4.186 | 5.0589
F-stat | 1305017.4929 | f | -0.43503 | 0.022966 | -18.9425 | -0.48083 | -0.38924
Date | Oct 13, 2004 | g | 0.015733 | 0.00094521 | 16.6454 | 0.013849 | 0.017618
Time | 4:11:59 AM
Based on results of the American Institute of Electric Engineers
Air at 760 mmHg, 25 C
Needle | Peak Volt | Diff |  |  | Diff
[cm] | [kV] | abs % | [kV] | [kV] | abs %
0.42 | 5 | 0.1218 | 5.0061 | 0.0060902 | 0.1218
0.85 | 10 | 1.9104 | 9.809 | -0.19104 | 1.9104
1.3 | 15 | 1.4145 | 15.2122 | 0.21217 | 1.4145
1.75 | 20 | 1.9211 | 20.3842 | 0.38423 | 1.9211
2.2 | 25 | 0.83612 | 25.209 | 0.20903 | 0.83612
2.69 | 30 | 0.2116 | 30.0635 | 0.06348 | 0.2116
3.2 | 35 | 0.8289 | 34.7099 | -0.29012 | 0.8289
3.81 | 40 | 0.52382 | 39.7905 | -0.20953 | 0.52382
4.49 | 45 | 0.14447 | 44.935 | -0.065009 | 0.14447
5.2 | 50 | 0.35046 | 49.8248 | -0.17523 | 0.35046
6.81 | 60 | 0.74914 | 59.5505 | -0.44948 | 0.74914
8.81 | 70 | 0.11486 | 69.9196 | -0.080403 | 0.11486
11.1 | 80 | 0.71857 | 80.5749 | 0.57486 | 0.71857
13.3 | 90 | 0.35138 | 90.3162 | 0.31624 | 0.35138
15.5 | 100 | 0.0097449 | 99.9903 | -0.0097449 | 0.0097449
17.7 | 110 | 0.16429 | 109.8193 | -0.18072 | 0.16429
19.8 | 120 | 0.46072 | 119.4471 | -0.55287 | 0.46072
22 | 130 | 0.13099 | 129.8297 | -0.17028 | 0.13099
24.1 | 140 | 0.015298 | 140.0214 | 0.021417 | 0.015298
26.1 | 150 | 0.02586 | 149.9612 | -0.03879 | 0.02586
28.1 | 160 | 0.060873 | 160.0974 | 0.097397 | 0.060873
30.1 | 170 | 0.23189 | 170.3942 | 0.39421 | 0.23189
32 | 180 | 0.1618 | 180.2912 | 0.29125 | 0.1618
33.9 | 190 | 0.14167 | 190.2692 | 0.26917 | 0.14167
35.7 | 200 | 0.11449 | 199.771 | -0.22898 | 0.11449
37.6 | 210 | 0.081443 | 209.829 | -0.17103 | 0.081443
39.5 | 220 | 0.047328 | 219.8959 | -0.10412 | 0.047328
41.4 | 230 | 0.019043 | 229.9562 | -0.043798 | 0.019043
43.3 | 240 | 0.00012912 | 239.9997 | -0.00030988 | 0.00012912
45.2 | 250 | 0.0086683 | 250.0217 | 0.021671 | 0.0086683
54.7 | 300 | 0.018057 | 300.0542 | 0.05417 | 0.018057
CORRECTIONS FOR TEMPERATURE AND PRESSURE
Values found in the above table may be corrected for temperature and pressure
by multiplying the values given by the appropriate correction factor found below:
Pressure [mmHg]
Temp. [C] | 720 | 740 | 760 | 780
0 | 1.04 | 1.06 | 1.09 | 1.12 |  | kV | cm
10 | 1 | 1.02 | 1.05 | 1.08 |  | 20 | 1.75
20 | 0.96 | 0.99 | 1.015 | 1.04 |  | 22.7778 | 2 | Interpolation
30 | 0.93 | 0.96 | 0.98 | 1.01 |  | 25 | 2.2
Interpolation for needle-points |  |  |  | Interpolation for 5cm balls
kV | cm |  |  | kV | cm
20 | 1.75 | Fixpoint 1 |  | 30 | 0.94 | Fixpoint 1
22.6596 | 2 | Interpolation |  | 31.6667 | 1 | Interpolation
30 | 2.69 | Fixpoint 2 |  | 40 | 1.3 | Fixpoint 2

## Fit2
SPARK-GAP VOLTAGES
C:\TCWIN4\CLIPBRD.WK1 |  |  | y=(a+cx+ex^2+gx^3+ix^4+kx^5)/(1+bx+dx^2+fx^3+hx^4+jx^5) [NL]
|  | Parameters | Values | Std Error | T Value | 95% Conf Lim | 95% Conf Lim
Eqn | y=(a+cx+ex^2+gx^3+ix^4+kx^5)/(1+bx+dx^2+fx^3+hx^4+jx^5) [NL] | a | -0.010794 | 1.251e-08 | -862812.0513 | -0.010794 | -0.010794
Eqn # | 7909 | b | -0.099541 | 5.1775e-06 | -19225.8335 | -0.099552 | -0.09953
r2 | 0.99999 | c | 11.7645 | 8.8234e-08 | 133333638.8412 | 11.7645 | 11.7645
DF Adj r2 | 0.99999 | d | 0.020972 | 2.665e-05 | 786.9444 | 0.020916 | 0.021028
Fit Std Err | 0.19242 | e | -1.1379 | 5.8244e-07 | -1953720.2799 | -1.1379 | -1.1379
F-stat | 216520.7188 | f | -0.0012705 | 2.7531e-06 | -461.4816 | -0.0012763 | -0.0012648
Date | Oct 13, 2004 | g | 0.13696 | 1.9525e-06 | 70144.466 | 0.13696 | 0.13696
Time | 5:16:39 AM | h | 2.2013e-05 | 6.5544e-07 | 33.5846 | 2.0646e-05 | 2.338e-05
|  | i | -0.0074392 | 1.8727e-05 | -397.2407 | -0.0074783 | -0.0074002
|  | j | 1.0283e-08 | 2.0693e-09 | 4.9694 | 5.9666e-09 | 1.4599e-08
|  | k | 0.00012805 | 3.1613e-06 | 40.5062 | 0.00012146 | 0.00013465
Based on results of the American Institute of Electric Engineers
Air at 760 mmHg, 25 C
Needle | Peak Volt | alte Diff |  |  | Diff
[cm] | [kV] | abs % | [kV] | [kV] | abs %
0.42 | 5 | 0.1218 | 4.9277 | -0.072251 | 1.445
0.85 | 10 | 1.9104 | 9.9457 | -0.054349 | 0.54349
1.3 | 15 | 1.4145 | 15.1002 | 0.10017 | 0.66782
1.75 | 20 | 1.9211 | 20.102 | 0.10195 | 0.50976
2.2 | 25 | 0.83612 | 24.9043 | -0.095708 | 0.38283
2.69 | 30 | 0.2116 | 29.8649 | -0.13512 | 0.45038
3.2 | 35 | 0.8289 | 34.6997 | -0.3003 | 0.858
3.81 | 40 | 0.52382 | 40.025 | 0.025035 | 0.062588
4.49 | 45 | 0.14447 | 45.3876 | 0.38764 | 0.86141
5.2 | 50 | 0.35046 | 50.3977 | 0.39769 | 0.79539
6.81 | 60 | 0.74914 | 60.0066 | 0.00656 | 0.010933
8.81 | 70 | 0.11486 | 69.886 | -0.11401 | 0.16288
11.1 | 80 | 0.71857 | 80.1301 | 0.13006 | 0.16257
13.3 | 90 | 0.35138 | 89.8353 | -0.16466 | 0.18296
15.5 | 100 | 0.0097449 | 99.7448 | -0.25516 | 0.25516
17.7 | 110 | 0.16429 | 109.9241 | -0.075889 | 0.06899
19.8 | 120 | 0.46072 | 119.8558 | -0.1442 | 0.12017
22 | 130 | 0.13099 | 130.3934 | 0.39345 | 0.30265
24.1 | 140 | 0.015298 | 140.4541 | 0.45413 | 0.32438
26.1 | 150 | 0.02586 | 149.9865 | -0.013456 | 0.0089705
28.1 | 160 | 0.060873 | 159.7367 | -0.2633 | 0.16456
30.1 | 170 | 0.23189 | 170.0104 | 0.010447 | 0.0061452
32 | 180 | 0.1618 | 180.071 | 0.071047 | 0.039471
33.9 | 190 | 0.14167 | 190.1904 | 0.1904 | 0.10021
35.7 | 200 | 0.11449 | 199.7641 | -0.23586 | 0.11793
37.6 | 210 | 0.081443 | 209.8505 | -0.14947 | 0.071175
39.5 | 220 | 0.047328 | 219.9244 | -0.075565 | 0.034348
41.4 | 230 | 0.019043 | 229.9922 | -0.0077717 | 0.003379
43.3 | 240 | 0.00012912 | 240.0576 | 0.057551 | 0.02398
45.2 | 250 | 0.0086683 | 250.122 | 0.12199 | 0.048795
54.7 | 300 | 0.018057 | 300.4237 | 0.42373 | 0.14124
| Max.% | 1.9211 |  |  | 1.445
| Min.% | 0.00012912 |  |  | 0.003379
| Avg.% | 0.38353 |  |  | 0.28799
CORRECTIONS FOR TEMPERATURE AND PRESSURE
Values found in the above table may be corrected for temperature and pressure
by multiplying the values given by the appropriate correction factor found below:
Pressure [mmHg]
Temp. [C] | 720 | 740 | 760 | 780
0 | 1.04 | 1.06 | 1.09 | 1.12 |  | kV | cm
10 | 1 | 1.02 | 1.05 | 1.08 |  | 20 | 1.75
20 | 0.96 | 0.99 | 1.015 | 1.04 |  | 22.7778 | 2 | Interpolation
30 | 0.93 | 0.96 | 0.98 | 1.01 |  | 25 | 2.2
Interpolation for needle-points |  |  |  | Interpolation for 5cm balls
kV | cm |  |  | kV | cm
20 | 1.75 | Fixpoint 1 |  | 30 | 0.94 | Fixpoint 1
22.6596 | 2 | Interpolation |  | 31.6667 | 1 | Interpolation
30 | 2.69 | Fixpoint 2 |  | 40 | 1.3 | Fixpoint 2

## Fit3
SPARK-GAP VOLTAGES
C:\TCWIN4\CLIPBRD.WK1 |  |  | y=(a+cx+ex^2+gx^3+ix^4+kx^5)/(1+bx+dx^2+fx^3+hx^4+jx^5) [NL]
|  | Parameters | Values | Std Error | T Value | 95% Conf Lim | 95% Conf Lim
Eqn | y=(a+cx+ex^2+gx^3+ix^4+kx^5)/(1+bx+dx^2+fx^3+hx^4+jx^5) [NL] | a | 0.10168 | 1.3223e-08 | 7689619.9111 | 0.10168 | 0.10168
Eqn # | 7909 | b | -0.10298 | 5.355e-06 | -19231.3261 | -0.103 | -0.10297
r2 | 0.99999 | c | 11.6098 | 9.1837e-08 | 126417237.0736 | 11.6098 | 11.6098
DF Adj r2 | 0.99999 | d | 0.022003 | 2.7363e-05 | 804.0936 | 0.021946 | 0.02206
Fit Std Err | 0.17111 | e | -1.1137 | 6.0018e-07 | -1855598.8114 | -1.1137 | -1.1137
F-stat | 253242.3348 | f | -0.0013154 | 2.748e-06 | -478.6766 | -0.0013211 | -0.0013097
Date | Oct 13, 2004 | g | 0.13948 | 1.9985e-06 | 69789.2758 | 0.13947 | 0.13948
Time | 5:37:34 AM | h | 2.2556e-05 | 6.5879e-07 | 34.238 | 2.1181e-05 | 2.393e-05
|  | i | -0.0075887 | 1.9086e-05 | -397.6103 | -0.0076285 | -0.0075489
|  | j | 9.01e-09 | 2.0535e-09 | 4.3876 | 4.7265e-09 | 1.3294e-08
|  | k | 0.00012968 | 3.2057e-06 | 40.4523 | 0.00012299 | 0.00013637
Based on results of the American Institute of Electric Engineers
Air at 760 mmHg, 25 C
|  |  | Fit3 | Fit3 | Fit2 | Fit1
Needle | Peak Volt |  | Diff | Diff | Diff | Diff
[cm] | [kV] | [kV] | [kV] | abs % | abs % | abs %
0.42 | 5 | 4.9883 | -0.011662 | 0.23324 | 1.445 | 0.1218
0.85 | 10 | 9.9693 | -0.030723 | 0.30723 | 0.54349 | 1.9104
1.3 | 15 | 15.1003 | 0.10034 | 0.66896 | 0.66782 | 1.4145
1.75 | 20 | 20.0911 | 0.091094 | 0.45547 | 0.50976 | 1.9211
2.2 | 25 | 24.8913 | -0.1087 | 0.43481 | 0.38283 | 0.83612
2.69 | 30 | 29.8557 | -0.14432 | 0.48107 | 0.45038 | 0.2116
3.2 | 35 | 34.6973 | -0.30269 | 0.86484 | 0.858 | 0.8289
3.81 | 40 | 40.0305 | 0.030484 | 0.07621 | 0.062588 | 0.52382
4.49 | 45 | 45.3982 | 0.39821 | 0.88492 | 0.86141 | 0.14447
5.2 | 50 | 50.4086 | 0.40858 | 0.81716 | 0.79539 | 0.35046
6.81 | 60 | 60.0061 | 0.0060799 | 0.010133 | 0.010933 | 0.74914
8.81 | 70 | 69.8723 | -0.12772 | 0.18246 | 0.16288 | 0.11486
11.1 | 80 | 80.1183 | 0.11833 | 0.14792 | 0.16257 | 0.71857
13.3 | 90 | 89.8352 | -0.16479 | 0.1831 | 0.18296 | 0.35138
15.5 | 100 | 99.7549 | -0.24507 | 0.24507 | 0.25516 | 0.0097449
17.7 | 110 | 109.9368 | -0.063233 | 0.057485 | 0.06899 | 0.16429
19.8 | 120 | 119.8623 | -0.13772 | 0.11477 | 0.12017 | 0.46072
22 | 130 | 130.3888 | 0.38878 | 0.29907 | 0.30265 | 0.13099
24.1 | 140 | 140.4481 | 0.44815 | 0.3201 | 0.32438 | 0.015298
26.1 | 150 | 149.9973 | -0.0026982 | 0.0017988 | 0.0089705 | 0.02586
28.1 | 160 | 159.7478 | -0.25223 | 0.15764 | 0.16456 | 0.060873
30.1 | 170 | 170.002 | 0.0020138 | 0.0011846 | 0.0061452 | 0.23189
32 | 180 | 180.064 | 0.064032 | 0.035573 | 0.039471 | 0.1618
33.9 | 190 | 190.1946 | 0.19457 | 0.10241 | 0.10021 | 0.14167
35.7 | 200 | 199.7754 | -0.2246 | 0.1123 | 0.11793 | 0.11449
37.6 | 210 | 209.8631 | -0.13687 | 0.065175 | 0.071175 | 0.081443
39.5 | 220 | 219.9336 | -0.066446 | 0.030203 | 0.034348 | 0.047328
41.4 | 230 | 229.9949 | -0.0050872 | 0.0022118 | 0.003379 | 0.019043
43.3 | 240 | 240.0523 | 0.052263 | 0.021776 | 0.02398 | 0.00012912
45.2 | 250 | 250.1082 | 0.10816 | 0.043264 | 0.048795 | 0.0086683
54.7 | 300 | 300.3761 | 0.3761 | 0.12537 | 0.14124 | 0.018057
|  |  | Max.% | 0.88492 | 1.445 | 1.9211
|  |  | Min.% | 0.0011846 | 0.003379 | 0.00012912
|  |  | Avg.% | 0.24138 | 0.28799 | 0.38353
CORRECTIONS FOR TEMPERATURE AND PRESSURE
Values found in the above table may be corrected for temperature and pressure
by multiplying the values given by the appropriate correction factor found below:
Pressure [mmHg]
Temp. [C] | 720 | 740 | 760 | 780
0 | 1.04 | 1.06 | 1.09 | 1.12 |  | kV | cm
10 | 1 | 1.02 | 1.05 | 1.08 |  | 20 | 1.75
20 | 0.96 | 0.99 | 1.015 | 1.04 |  | 22.7778 | 2 | Interpolation
30 | 0.93 | 0.96 | 0.98 | 1.01 |  | 25 | 2.2
Interpolation for needle-points |  |  |  | Interpolation for 5cm balls
kV | cm |  |  | kV | cm
20 | 1.75 | Fixpoint 1 |  | 30 | 0.94 | Fixpoint 1
22.6596 | 2 | Interpolation |  | 31.6667 | 1 | Interpolation
30 | 2.69 | Fixpoint 2 |  | 40 | 1.3 | Fixpoint 2